## Slide 1
RESEARCH INITIATION PROJECT — FINAL PRESENTATION
Finding Failing Transformers Without Labels
Label-free health monitoring from dissolved-gas analysis — and a hidden trap in how such models are validated.
Thibaut Faucheux — CESI Engineering School, France
Supervised by Dr. Rattanakorn Phadungthin — KMUTNB, Bangkok, Thailand
July 2026 · 5-week research project

## Slide 2
PLAN
What the next 20 minutes look like
01
Context — transformers, gas analysis, and a fleet with no labels
02
Contribution 1 — a fault-type map learned without labels
03
Contribution 2 — the validation trap: surveillance bias
04
Contribution 3 — a fleet risk index + live dashboard demo
05
Take-aways — for the field, and for me
CESI × KMUTNB — Research Initiation 2026
2

## Slide 3
1 · CONTEXT
A blood test for transformers
Power transformers are critical, million-euro assets. When something goes wrong inside — overheating, sparking, arcing — the insulating oil breaks down and releases dissolved gases. Measuring them is called DGA: Dissolved Gas Analysis.
Transformer
fault heats the oil
Gases dissolve in oil
Lab: 7 gases (ppm)
Each gas is a clue:
H2 — sparking
C2H2 — arcing (worst)
C2H4/CH4 — overheating
CO/CO2 — paper ageing
CESI × KMUTNB — Research Initiation 2026
3

## Slide 4
1 · CONTEXT
The problem: experts are scarce, labels don't exist
The Duval Triangle — an expert rule from the 1970s, still the industry standard.
Expert rules (Duval, IEC ratios) work — but need an expert, and often answer “undetermined”.
Machine learning reaches 99% accuracy in papers — but needs labelled faults, which utilities almost never have.
Our fleet: zero confirmed fault labels. Just gas numbers and messy operator notes.
Goal: rank 628 transformers by risk and read fault types — using no labels at all.
CESI × KMUTNB — Research Initiation 2026
4

## Slide 5
1 · CONTEXT
Real fleet data — not a curated benchmark
628
transformers in service
4,563
oil samples analysed
5 yrs
of history (2019–2024)
42
manufacturers
What “real” means here
Gas values stored as text, with dashes for missing
Operator notes mix English and Thai — 69% contain Thai
Notes log everything: faults, but mostly maintenance and admin
No ground truth; assembled from multiple sources, anonymised
Why that is interesting
Most published methods are tested on small, clean, balanced datasets (often under 200 samples). Whether they survive contact with a real fleet is exactly the open question — and the messiness itself hides a scientific finding.
CESI × KMUTNB — Research Initiation 2026
5

## Slide 6
1 · CONTEXT
Five weeks that did not go as planned — on purpose
Week 1
Clean the data,
rebuild expert rules
Week 2
First models +
a fleet risk index
Week 3 — discovery
Our validation label is biased.
Everything re-examined.
Week 4
Attack our own results: simpler
wins; Thai notes translated
Week 5
IEEE paper, dashboard,
this defense
Research is not a straight line. Our two strongest findings came from questioning our own results — not from the original plan.
CESI × KMUTNB — Research Initiation 2026
6

## Slide 7
2 · CONTRIBUTION 1 — FAULT TYPES WITHOUT LABELS
The severity trap
Feed raw gas concentrations to any model, and it learns “how much gas” — not “which fault”. The same fault at low and high gassing looks like two different things.
Concentrations (ppm)
arcing, early
arcing, severe
same fault — far apart
Proportions (the gas “recipe”)
same fault — same place
FOR THE EXPERTS
A plain autoencoder on log-concentrations encodes magnitude: total gas is linearly readable from its 2-D latent (R² = 0.63), and agreement with Duval classes is near-noise (ARI 0.14–0.16).
CESI × KMUTNB — Research Initiation 2026
7

## Slide 8
2 · CONTRIBUTION 1 — FAULT TYPES WITHOUT LABELS
Use the right geometry, and fault types appear
Agreement with the expert (Duval) classes, from raw inputs to our representation.
0.16 → 0.55
agreement with expert diagnosis (ARI) — 3.4× better, with zero labels
The trick is not a bigger model. It is treating gas proportions with the mathematics made for proportions (log-ratios), then the simplest possible projection.
FOR THE EXPERTS
Centred log-ratio (Aitchison) on the 5 combustible gases → standardise → PCA-2 → KMeans (k=7). ARI 0.545 ± 0.002 vs Duval. Deterministic. Holds on a temporal split: fit pre-2022, score 2022+ → ARI 0.45.
CESI × KMUTNB — Research Initiation 2026
8

## Slide 9
2 · CONTRIBUTION 1 — FAULT TYPES WITHOUT LABELS
A data-driven diagnostic map — and an honest negative
Every dot is an oil sample. Colours = expert diagnosis, added afterwards — the map itself never saw them.
Discharge, partial-discharge and thermal regions emerge on their own
Readable axes — an engineer can interpret the directions
Deterministic: same data in, same map out
NEGATIVE RESULT
We also built a deep autoencoder (SD-CAE) and an adversarial variant. Neither beat the simple linear map. We report both as negatives — knowing what does not work is a result too.
CESI × KMUTNB — Research Initiation 2026
9

## Slide 10
3 · CONTRIBUTION 2 — THE VALIDATION TRAP
“The more you look, the more you find”
To check our risk score, we used the only “truth” available: operator-logged field events. Then we noticed something wrong.
Operator worries
about a transformer
Samples it more
extra oil tests
Logs more notes
events get recorded
“Risky” in the data
the loop feeds itself
the loop feeds itself — attention, not chemistry
FOR THE EXPERTS
This is surveillance / informed-presence bias, well known in medicine and health records (Sackett 1979; Haut & Pronovost 2011; Goldstein 2016). To our knowledge, never reported for DGA — models in this field are routinely validated against such labels.
CESI × KMUTNB — Research Initiation 2026
10

## Slide 11
3 · CONTRIBUTION 2 — THE VALIDATION TRAP
Three tests, one verdict
(a) The tie. Counting how often a unit was sampled predicts logged events as well as all our chemistry combined (0.76 vs 0.74 — statistically indistinguishable).
(b) No foresight. Control for the sample count, and the score's ability to predict future events drops to a coin flip (0.50).
(c) The fix. Define the target by chemistry (arcing onset) instead of attention — now gases predict (0.64) and the count does not (0.49).
CESI × KMUTNB — Research Initiation 2026
11

## Slide 12
3 · CONTRIBUTION 2 — THE VALIDATION TRAP
Repairing the label: 211 Thai notes, read one by one
69%
of operator notes contain Thai — invisible to the English keyword filter
211
distinct Thai notes translated and classified (released for expert validation)
+6
genuine electrical events recovered (noise, breaker explosions, insulation symptoms)
Example finds
“หม้อแปลงมีเสียงดัง” — transformer making abnormal noise
“ตามผลเนื่องจาก Bkr. ระเบิด” — follow-up after breaker explosion
“ค่า p.f สูง” — high insulation power factor
The punchline
On the repaired label, the sample-count's advantage disappears entirely (0.734 vs 0.735). Part of the “trap” was simply that the label was incomplete — in a language the pipeline didn't read.
CESI × KMUTNB — Research Initiation 2026
12

## Slide 13
4 · CONTRIBUTION 3 — FROM RESEARCH TO PRACTICE
A triage list for the maintenance team
Fleet sorted into 10 risk groups by our label-free index. Real logged events concentrate exactly where the index says they should.
27%
event rate in the riskiest 10% of the fleet…
2%
…versus the safest 10%
Four transparent ingredients: gas severity, acetylene (arcing), the speed of hydrogen rise, and statistical novelty. No black box — and always reported together with the surveillance-bias floor from the previous slides.
CESI × KMUTNB — Research Initiation 2026
13

## Slide 14
4 · CONTRIBUTION 3 — FROM RESEARCH TO PRACTICE
DEMO
The whole project, live
1. Fleet ranking — 628 units re-ranked live as we switch scoring profile
2. Transformer inspector — gas history, expert diagnoses, “why this score”
3. The fault-type map and the surveillance-bias evidence — the paper, interactive
localhost:8501 — runs on the anonymised dataset · if the demo gods object, every view also exists as a paper figure
CESI × KMUTNB — Research Initiation 2026
14

## Slide 15
5 · TAKE-AWAYS
What this project says to the field
1
The right geometry beats a bigger model.
A linear method in the correct mathematical space outperformed deep networks — simpler, interpretable, deployable.
2
Validation labels can lie.
Any DGA risk model validated on operator-logged events should report the sample-count “confound floor” — otherwise surveillance can be mistaken for diagnostic skill.
3
Honest negatives are results.
Deep SVDD, VAE, adversarial disentanglement, RUL modelling: tested, rejected, documented. Future work starts further ahead.
Deliverables: a 6-page IEEE paper draft (3 contributions) · a reproducible pipeline (one command regenerates every number, 10 automated tests) · an anonymised public dataset extract · the interactive dashboard.
CESI × KMUTNB — Research Initiation 2026
15

## Slide 16
5 · TAKE-AWAYS
What five weeks of research taught me
The scientific method, for real — hypothesis, test, and the discipline to pivot when the evidence disagrees with the plan
Statistical honesty — confidence intervals, paired tests, blocked bootstraps; “0.76 vs 0.74” means nothing until you test it
Attack your own results first — the finding that a simple method beat our own headline model came from auditing ourselves before reviewers would
A full research stack — Python/PyTorch, statistics, LaTeX/IEEE writing, git, automated testing, Streamlit
Working across languages and cultures — a French student, a Thai fleet, English science; 211 Thai field notes read and classified
Scoping — five weeks forces choices: what to cut, what to consolidate, what to hand to future work
CESI × KMUTNB — Research Initiation 2026
16

## Slide 17
THANK YOU
Questions?
Thibaut Faucheux · CESI × KMUTNB
With thanks to Dr. Rattanakorn Phadungthin for the supervision and domain guidance.
628 transformers · 4,563 samples · ARI 0.16 → 0.55 without labels · one validation trap exposed · 6-page IEEE paper · live dashboard