# Label-Free Transformer Health Monitoring from DGA — and a Caution About Validation

Thibaut Faucheux (CESI, FISA4 INFO) · Research Initiation at KMUTNB, Bangkok · Supervisor: Dr. Rattanakorn Phadungthin

End-of-project report — Weeks 1 to 5 — 17 July 2026

Executive summary. Power transformers fail expensively, and Dissolved Gas Analysis (DGA) is the standard way to catch faults early. Conventional interpretation (Duval, IEC, Rogers) is rule-based, needs an expert, and machine-learning alternatives need fault labels that utilities rarely have. On a real longitudinal fleet (628 units, 4,563 samples, 2019–2024) this project delivered three results, all label-free. (1) Representing each sample by the log-ratios of its gas composition separates fault type from gassing severity by construction: a simple linear projection of that representation agrees with the expert Duval classes at ARI 0.55, versus 0.16 for raw concentrations — and a neural autoencoder adds nothing, a negative result we report. (2) We discovered that the field-event notes routinely used to validate such models are confounded by surveillance bias: simply counting how often a unit was sampled predicts logged events as well as all our chemistry combined (AUC 0.76 vs 0.74, statistically indistinguishable). We quantify the confound, repair part of it by translating the Thai field notes, and propose a confound-free, chemistry-defined evaluation target. (3) A label-free health/risk index ranks the fleet usefully (riskiest decile ≈ 27% event rate vs 2% for the safest), reported honestly against the confound floor.

## 1. Context and motivation

Power transformers are among the most critical and expensive assets of an electrical grid; an in-service failure means outages, safety risk and costly, slow replacement. Dissolved Gas Analysis (DGA) detects incipient faults early: internal thermal or electrical stress decomposes the oil and paper insulation and releases characteristic gases (hydrogen, methane, ethylene, acetylene, carbon oxides) measured in ppm. Conventional interpretation — IEC 60599 ratios, Rogers ratios and the Duval Triangle — is rule-based, requires expert judgement, sometimes returns “not determined”, and published machine-learning methods assume per-sample fault labels that utilities rarely have at scale. In practice an operator must prioritise maintenance across an entire fleet — rank units by risk — without labels. That is the gap this project addresses.

## 2. Objective, research question and dataset

Research question. Can we rank transformers across a fleet by incipient-fault risk and recover fault types, label-free, from each unit’s DGA history — and can we trust the way such models are usually validated?

Dataset. 628 transformers, 4,563 main-tank oil samples, 42 manufacturers, spanning ~5 years (2019–2024) at ~6-month sampling intervals (a genuinely longitudinal fleet), assembled from multiple operational sources in Thailand and anonymised. 391 samples carry a free-text field-event note (Buchholz trip, bushing failure, high power factor…) — 69% of them partly in Thai — used as weak validation labels, whose reliability itself became a finding of the project.

## 3. Week-by-week progress

| Week | Dates | Theme | Main outcome |
| --- | --- | --- | --- |
| 1 | 15–19 Jun | Foundations | Clean data + EDA, conventional baselines, literature (15+ refs with notes), problem statement; the “severity trap” identified |
| 2 | 22–26 Jun | Models + the discovery | Label-free risk index (AUC 0.74); research campaign reveals surveillance bias in the validation label (sample count: AUC 0.76); project reframed |
| 3 | 29 Jun–3 Jul | Attacking our own results | Linear CLR-PCA beats the neural model (ARI 0.545 vs 0.474); statistics hardened (unit-blocked intervals); 211 Thai notes translated; paper rewritten; git repository + dashboard |
| 4 | 6–10 Jul | Consolidation | Dashboard UX redesign; data-provenance statement; paper figures consolidated to the 6-page IEEE limit; defense decks (HTML + PowerPoint) |
| 5 | 13–17 Jul | Dissemination | Final report, cross-deliverable coherence audit, rehearsal, defense |

Week 1 — Foundations. Built and verified the full pipeline end-to-end on the real data: cleaning (gas values stored as text, missing markers, field notes), exploratory analysis, and the conventional baselines (Duval / IEC / Rogers) reproduced as the reference to compare against. A first experiment already exposed the severity trap: a plain autoencoder on concentrations reaches near-perfect cluster quality scores while agreeing with expert fault types at only ARI ≈ 0.015 — it had learned how much gas, not which fault.

Conventional Duval diagnosis across the fleet — the baseline to compare against, with strong class imbalance.

Week 2 — Models, and the discovery that reframed the project. Built the label-free health/risk index (gas severity + acetylene weighting + hydrogen growth rate + anomaly score; AUC 0.74 against field events) and the compositional fault-type representation. Then a systematic research pass produced the project’s central finding: how often a unit is sampled predicts logged events as well as the chemistry does (AUC 0.76) — because operators re-sample units they worry about, the validation label partly records attention, not faults. This is surveillance / informed-presence bias, well documented in medicine but, to our knowledge, never reported for DGA. The project was reframed around it.

Week 3 — Attacking our own results. A full adversarial audit of our own headline claims. Outcome 1: the fault-type gain comes from the log-ratio geometry, not the neural network — a deterministic linear pipeline (CLR + PCA + KMeans) reaches ARI 0.545 ± 0.002 vs Duval, beating our own autoencoder (0.474 ± 0.055), which we demoted to a negative ablation. Outcome 2: honest statistics everywhere — the 0.76-vs-0.74 gap is not significant (p = 0.58); the physics carries a small real increment beyond the count (likelihood-ratio p = 0.003) but none forward in time; the confound-free arcing-onset target rests on 17 onset units, so we report unit-blocked confidence intervals (ethylene AUC 0.64, CI 0.52–0.77 — above chance, modest). Outcome 3: all 211 distinct Thai notes translated and classified (+6 genuine electrical events); on the repaired label the count’s advantage disappears entirely (0.734 vs 0.735) — part of the confound was label incompleteness. The paper was rewritten accordingly; the repository gained version control, automated tests and an interactive dashboard.

Fault-type agreement across representations: the gain is the log-ratio geometry, and a linear projection beats the autoencoder (negative ablation).

The learned diagnostic map — PCA of the standardised CLR, coloured by expert (Duval) class added afterwards: discharge, thermal and partial-discharge regions separate without any labels.

Week 4 — Consolidation. Dashboard redesigned around scoring profiles (usable by a non-expert); data-provenance statement finalised with the supervisor (anonymised multi-source records; an anonymised extract is released with the code); paper figures consolidated into two multi-panel figures to meet the 6-page IEEE limit; defense decks built (self-contained HTML + native PowerPoint).

Week 5 — Dissemination. This report, a cross-deliverable coherence audit (paper, decks, lab notebook, dashboard, repository), rehearsal and defense.

## 4. Key results

The surveillance-bias analysis. (a) A trivial sample count matches the physics index against the field-note label. (b) Temporal hold-out: forward validity vanishes once the count is controlled. (c) A confound-free chemistry target (arcing onset): gases predict, the count does not.

- Fault-type recovery (contribution 1): ARI 0.16 → 0.55 vs the Duval classes using log-ratio geometry and a linear projection; deterministic; stable on a strict temporal split (fit pre-2022, score 2022+: ARI 0.45). The neural variant (SD-CAE) and an adversarial disentanglement term are reported as negative results.

- The validation caution (contribution 2): sample count AUC 0.76 ≈ physics 0.74 (p = 0.58); forward validity falls to chance (0.50) once the count is controlled; a chemistry-defined target (arcing onset) remains genuinely predictable from gases (AUC 0.64, unit-blocked CI 0.52–0.77) while the count is not (0.49). Recommendation to the field: any DGA risk model validated on operator-logged events should co-report this sample-count confound floor.

- Fleet ranking (contribution 3): riskiest decile ≈ 27% event rate vs ≈ 2% for the safest; four transparent components (severity, acetylene, H2 growth rate, anomaly) — always read against the 0.76 floor above.

Field-event rate by risk decile: events concentrate where the label-free index says they should.

## 5. Conclusion

The project set out to rank a transformer fleet by risk without labels; it delivered that — and something arguably more valuable: evidence that the standard way of validating such models is partly measuring operator attention rather than transformer health, plus a practical fix (condition on the sampling count; use chemistry-defined targets; repair multilingual labels). Methodologically, the strongest lesson is that the right geometry beat the bigger model: a linear, interpretable, deterministic method outperformed our own neural network once the data was represented correctly. All claims are reproducible: one command regenerates every number and figure (10 automated tests), the paper draft (6-page IEEE format) is written, and an interactive dashboard exposes the whole framework on an anonymised data extract.

## 6. Limitations and next steps

- One fleet: the surveillance-bias finding is demonstrated on this fleet; its prevalence across utilities is an open (and testable) question.

- Weak labels remain weak: the Thai-note classification awaits full domain validation; real failure/maintenance records would strengthen every risk claim.

- Moderate absolute agreement: ARI 0.55 is against a heuristic (Duval), not ground truth; we claim the relative gain and the label-free setting, not diagnostic accuracy.

- Small-event statistics: the chemistry target has 17 onset units; intervals are wide and reported as such.

- Forward direction: trajectory features in the compositional plane (an honest “temporal representation”), federated evaluation across utilities, and prognostics once better labels exist.

Reproducible: every figure and number in this report is produced by versioned code (run_all.py regenerates all of them). Repository: github.com/Thibaut0000/DGA_KMUTNB_2026_ThibautFCX (private; anonymised data extract included). This is a research initiation (5 weeks, one student); results are honestly hedged.