# Week 1 Synthesis — Label-Free Health Ranking of Power Transformers from DGA

Thibaut Faucheux (CESI) · Host lab: KMUTNB, Bangkok · Supervisor: Dr. Rattanakorn Phadungthin

19 June 2026

## 1. The project in one paragraph

Power transformers are expensive, critical machines. Dissolved Gas Analysis (DGA) is like a blood test of the insulating oil: when a transformer has an early fault, it produces specific gases. Today engineers read these gases with fixed rules (Duval, IEC, Rogers). These rules need an expert, sometimes give “no answer”, and do not scale to a whole fleet. My project ranks a whole fleet of transformers by risk, without any fault labels — the computer learns the patterns by itself (self-supervised) and uses the history of each unit over time (temporal). I then compare this ranking with the conventional methods.

The pipeline: from each transformer’s DGA history to a risk-ranked fleet, with no fault labels.

## 2. What I understood

- The data has no labels and is longitudinal. 628 transformers, 4,563 oil samples, ~4.5 years, ~7 samples per unit. We do not know the “true” fault, so supervised learning is not realistic — the right goal is to rank units by risk.

- Each gas has a meaning. Hydrogen = partial discharge; methane/ethane = low-temperature heating; ethylene = high-temperature heating; acetylene = arcing = the most dangerous; CO/CO2 = paper damage.

- Conventional methods are a baseline, not the truth. Running Duval on the fleet gives mostly partial-discharge and thermal faults, with a strong class imbalance and some “not determined” cases.

- The key question: can a model rank the riskiest units — and does it capture the fault type, or only the overall severity (how much gas)?

What the conventional Duval rule says about the fleet — a baseline to compare against, with clear class imbalance.

## 3. What I did (Week 1)

- Built the full project and pipeline (data cleaning -> preprocessing -> conventional baselines -> autoencoder -> clustering -> anomaly detection -> evaluation). It runs end-to-end and is reproducible.

- Read the key reference papers and organised the references.

- Got two main results:

Finding 1 — the model can separate fault type from severity. A plain autoencoder mostly captures how much gas there is (severity), not which fault it is. Using the gas composition (proportions) instead makes the model agree far better with Duval fault types: agreement score ARI 0.14 -> 0.47.

Left: agreement with Duval fault type (higher is better) jumps with the compositional representation. Right: a plain model mostly encodes severity.

Finding 2 — the label-free risk ranking works. I built a risk score (severity + anomaly + acetylene weighting + time trend) and ranked the fleet. The 10% riskiest units have ~30% real fault-events, versus the 11.3% fleet average and only ~2-3% for the safest units. Overall AUC = 0.74 (a simple TCG-only baseline = 0.52).

Riskiest units (left, D1) carry many more real field faults than safe units (right, D10) — the ranking is meaningful.

## 4. What I plan to do (Weeks 2–5)

- Weeks 2–3: finish the per-unit temporal features and the full health/risk index; add a stronger anomaly method (Deep SVDD).

- Week 4: systematic comparison of my ranking against C57.104 / IEC / Rogers / Duval; show the units the rules miss; freeze the results and figures.

- Week 5: write the IEEE paper and prepare the defense.

- Open question to settle: how much the temporal (time-trend) information improves the ranking — early result is a small but positive gain.

## 5. Document analysis (the references I am using)

A one-line note on each key source, with what it contains:

- Ramarao et al. 2026 — review (34 pages). A survey of DGA diagnostics from classic rules to AI; gives the big picture and shows where my approach fits. My main related-work map.

- Saleh et al. 2026. A recent method that combines the classic rules with machine learning to classify faults (~99% accuracy, but it needs labelled data). My state-of-the-art comparison.

- Wang et al. 2016. Uses an autoencoder to learn features from gas data — the closest existing idea to mine, but it still ends with a labelled classifier.

- Liu et al. 2020. Groups transformers by fault using density clustering on gas proportions — the closest existing “no-label grouping” work.

- Duval 2002. Defines the Duval Triangle and the fault types (partial discharge, thermal, arcing) — the expert rule I compare against.

- IEEE C57.104-2019 (standard). Says when gas levels are “normal” using statistical limits — the basis for my severity / anomaly thresholds.

- IEC 60599:2022 (standard). The source of the gas-ratio rules (cited; not needed in full).

All numbers are produced by code and saved under results/; nothing is hand-typed. This is a Week-1 status — results are early and validated indirectly (no ground-truth health label exists).

## Appendix — the pipeline in code (one line per step)

Just to show that each step above is a short, reproducible piece of code. No need to read the code in detail — the plain-English line under each box says what it does. (Imports are omitted for clarity.)

1. Clean the data

df = data.load_clean()

Reads the 4,563 oil-test samples, fixes the formats, and marks the rows that carry a field-event note.

2. Prepare the data

fm = preprocessing.build_feature_matrix(df, cfg)

Puts the gas values on a comparable scale so the model can use them.

3. Conventional baseline

diag = conventional.diagnose(df)        # the classic Duval / IEC / Rogers expert rules

Applies the standard expert rules — this is what we compare our method against.

4. Self-supervised model

res = train_autoencoder(fm.X, cfg.autoencoder)   # the model learns gas patterns by itself
Z   = res.model.encode(fm.X)                      # a short "summary" of each sample

A small neural network learns the patterns on its own, with no labels, and summarizes each sample.

5. Grouping (clustering)

cl = clustering.fit(Z, cfg.clustering)

Automatically groups similar transformers into families.

6. Anomaly detection

scores = anomaly.reconstruction_scores(res.model, fm.X)   # how unusual each sample is
flags  = anomaly.threshold_flags(scores, 0.95)            # flag the most unusual 5%

Flags the most unusual samples — the candidate early faults.

7. Evaluation

evaluation.external_metrics(cl.labels, diag["duval"])     # our groups vs the expert diagnosis

Checks whether the model’s groups match the conventional expert diagnosis.

In short: the whole method is only a handful of short, transparent, reproducible code steps.